## Sheet1
UBC REAP Energy Modelling Guideline Checklist
Note: All units are expressed as IP units unless otherwise indicated.
Topic | Check | Comments | Met | Not Met | N/A
Building Envelope
Thermal performance of above-grade walls and roofs | Confirm that all similar wall- and roof-type assemblies that have been combined have an R-value within R-2 of one another. | List the weighted average U-value for the wall and roof assemblies. Values broken out by façade can be obtained from the LV-D report in the .SIM file: N - S - E - W - Total - Roof -
| Have the wall and roof thermal assemblies been quantified by a building envelope specialist? If no, confirm that the overall assembly reflects the framing included in drawings or in Table 1 of the guideline. For spandrel panels, use FRAMEplus online. |  | 0
Fenestration performance | Confirm that the window performance includes the impact of window framing and size?
| Have the window thermal performance been quantified by a building envelope specialist? If no, has a manufacturer quantified the thermal performance based on CSA A440.2 or NFRC 100 testing? If no, have the window assemblies been informed by a FRAMEPlus Online simulation (or equivalent) - as per instructions listed in the guideline? If the window assembly is not available within FRAMEplus online, refer to ASHRAE Fundamentals for specific window type and performance. | Identify the applicable compliance path. List the weighted average U-value for the window assemblie. Values broken out by façade can be obtained from the LV-D report in the .SIM file: N - S - E - W -
Confirm that all similar window types (i.e. fixed, operable, etc…) that have been combined have an U-value of 0.10 and a SHGC of 0.05 of one another.
Below-grade walls | Below grade walls have been included in energy simulation
Window-to-wall (WWR) ratio | Check that the calculated WWR matches the values identified in the drawings or provided by the architect. | For the different orientations, list the window area and calculate the WWR: N - S - E - W - Total -
Balconies | Verify that thermal impact of balconies is taken into account: - check that a separate wall assembly is created for large balconies (when the penetration cross-sectional area exceeds 2% of the above grade building envelope area) - check that the R-value of the assembly is calculated using a heat transfer calculator or is using the recommended value of R-1. | Percentage of balcony area (if applicable): Model R-value for balcony area (if applicable):
Exterior shading devices | Check if the geometry of proposed design windows includes exterior shading devices like canopies, balconies, and building extensions
Central Plant Equipment
Boiler parameters | Confirm that the number of boilers and sizing (shown in drawings/cut sheets/equipment schedules) reflects the PV-A report | Not applicable for buildings serviced by DE
| For condensing boilers, confirm that the efficiencies reflect the return water temperature for the design. For condensing boilers with outdoor air temperature reset, confirm that the boiler efficiency is weighted based on outdoor air temperature. | Provide boiler curves and verify return water temperature. Not applicable for buildings serviced by DE.
Chiller parameters | Verify that the chiller parameters reflect the equipment schedule/cut sheet: - check that the size of the chiller(s) shown in the PV-A report matches the total capacity of the cooling plant - check that the COP/output is entered at ARI 550/590 test conditions
Cooling tower parameters | Verify that the cooling tower parameters reflect the equipment schedule/cut sheet: - check that the size of the cooling tower(s) shown in the PV-A report matches the total capacity of the cooling towers - check that the design temperatures matches the manufacturer cut sheet
Pumps (hot water, chilled water and condenser pumps) | Verify that the pump parameters reflect the equipment schedule/cut sheet: - check temperature drop/rise of heating/cooling pumps is calculated based on the plant capacity - for EE4, ensure that the hot water and chilled water pump power are modelled as per the EE4 Modelling Guidelines - otherwise, ensure that pump power is consistent with the sum of design pump brake horsepower (BHP) - ensure that non-HVAC pumps (i.e. sump, storm, sanitary) are included in the EUI calculation.
Service hot water loads | Make sure to account for all fixtures such as janitor and kitchen sinks
District energy systems (DES) | Verify Method 1 is used, as described in the LEED Canada supplemental guidance for DES systems.
Building Zoning
Zoning | Verify that the zoning reflects as-designed HVAC zoning
HVAC Systems
Equipment capacities | Verify that the equipment capacities reflect the equipment schedule/cut sheet
Fan power | Verify that the design fan power calculation includes the motor efficiency
Ventilation air heat recovery | Verify that heat recovery calculation accounts for differing supply and exhaust airflows.
Outdoor air rates | Verify that outdoor air rates are are in compliance with the ventilation rate procedure of ASHRAE 62.1 (or the authority having jurisdiction)
Verify if the proposed total building ventilation rate does not exceed the total building code ventilation rate by more than 20%
Verify the OA rates produced by the output report are consistent with design
Demand control ventilation (DCV) | Verify that the DCV has been modelled according to the methodology described in the LEED Canada supplemental guidance for energy modelling
Fan schedule | Verify that the fan schedule used in all the zones served by one HVAC system is the same
Economizers | Verify that the economizers reflect the actual design
Lighting
Daylighting and automatic lighting controls | Verify that the daylight and occupancy sensors have been modelled in accordance with Section 8.1.1 of the EE4 Modelling Guide. Due to prevalence of residential plug in lamps,in-suite lighting should be modelled to code and no credit taken.
Lighting systems | Verify that the ballast power is included in the power of lighting systems
Exterior and parking lighting | Verify that exterior and parking lighting system energy have been included in the EUI calculation.
Building Specific
Residential - plug loads | For residential buildings, verify that the energy consumption from appliances is included in the simulation results
General
Energy rates | Provide a description of utility rates used in the model.
Building orientation | Verify that the building orientation in the model reflects the actual orientation
Note on C5: Author: EE4/Equest specific Other models may not be able to provide3 Total wall, roof, floor?, total
Note on C8: Author: façade averages not needed

## Sheet2
156350
14.8905